## Slide 1: The Hardware-in-the-loop Testbed for Microgrid
Jun Zhang
Graduate Research Assistant
Electrical Engineering & Computer Science
Daktronics Engineering Hall 314

## Slide 2: Why HIL?
HIL is closer to reality
 | HIL | Software Simulation
Synchronization | Not guarantee (fit reality) | Always guarantee
Communication | Real protocol with delay(fit reality) | No protocol and virtual delay
Measurement | Real sensors with bias, error and delay (fit reality) | Virtual sensor
Simulation speed | Real time (fit reality) | Virtual time (slow)
Cost-efficiency | Low | High
HIL Simulation: validate a control system's design by running the control on its actual hardware

## Slide 3: Testbed structure
  Testbed overview
  System data flow
Simulator: model the inverters, measurements, and the power grid in real time
OP8666: DSP controller
Monitor and Oscilloscope: Data monitoring

## Slide 4: Control Structure
    Control blocks in DSP
      Zero-level control: tracks the control set points
      Grid synchronization control: mitigates the impulse current when an inverter is connected to the grid
      Droop control: supports the grid voltage and frequency without communication (time step: 50 s)
      Optimal secondary control: optimizes the system’s voltage and frequency, and achieves proportional power sharing (time step: 0.025 s)

## Slide 5: Communication & cores ASSIGNMENT
core1
core2
Primary Control
Secondary Control
Serial
Communication 1
Serial
Communication 2
Global RAM
    Communication
      Bidirected communication: use two set of transmitter and receiver to have bidirected communication.
      Time step: 0.025s
    Cores assignment
      Core1: primary control, secondary control and clockwise communication
      Core2: counterclockwise communication
      Communication between core1 and core2 by global RAM

## Slide 6: Simulation result
1
2
3
4
5
1
Inverter 1 black starts
2
3
4
Inverters 2,3, and 4 plugin
5
Load changes
    1. Black start in droop mode:
1
2
3
4
5
  System under droop mode

## Slide 7: Simulation result
1
Running in droop mode
2
Mode change
    2. Switch to optimal control:
1
2
3
3
Load changes
Restore the frequency to 60 Hz
Admissible voltage profile
  System under optimal control

## Slide 8: Simulation result
1
Running in droop mode
2
Mode change
    2.Shift to the proposed control:
1
2
3
3
Load changes
Better reactive power sharing
Perfect active power sharing

## Slide 9: Q & A
Thanks for your listening!